## Cohorts
| Primary | Primary | Primary | Secondary | Primary | Secondary | Secondary
cohort ref | Material | Diameter | Install Yr Band | Sec Install Yr Band | Function | Hotspot DAZ | DAZ | Total length (km) | Total ave bursts per yr | Nominal expected bursts | Annual burst rate tolerance | Tolerance | Within tolerance | Average annual bursts per 1000km | Grade | Rank | If not within tolerance, state reasons:
1 | AC | <=320mm | (1900-2010] | Not used | C | Not used | Not used | 28.8577 | 1.8 | 2.5 | 0.28 | +/- 50% | Yes | 62.375 | 3 | 20
2 | AC | <=320mm | (1900-2010] | Not used | F | Not used | Not used | 44.9704 | 1.2 | 2.5 | 0.52 | +/- 50% | No | 26.6842 | 2 | 37 | Aggregation with the following cohort (ref 3) and splitting by Hotspot DAZ = Yes/No does not rectify the problem of cohorts 2 and 3 being outside of the lower and upper tolerance bounds, respectively.
3 | AC | <=320mm | 2011 onwards | Not used | F | Not used | Not used | 1.8272 | 4 | 2.5 | -0.6 | +/- 50% | No | 2189.1004 | 5 | 3 | This cohort comprises four DAZs but all four bursts fall within the same DAZ. Splitting this DAZ out would not reduce the failure rate p.a and would introduce an additional cohort having a zero failure history.
4 | AC | >320mm | 1901 onwards | Not used | C | Not used | Not used | 11.4639 | 3.2 | 1 | -2.2 | +/- 50% | No | 279.1364 | 5 | 8 | Cohort comprises all rising mains of this material, size and function.
5 | CI | <=320mm | (1900-1980] | Not used | C | Yes | 206, 273, 301-02, 376, 434, 612 | 3.2953 | 2 | 2.5 | 0.2 | +/- 50% | Yes | 606.9209 | 5 | 5
6 | CI | <=320mm | (1900-1980] | Not used | C | Yes | 711, 748, 752, 758, 756 | 3.028 | 2.2 | 2.5 | 0.12 | +/- 50% | Yes | 726.5431 | 5 | 4
7 | CI | <=320mm | (1900-1980] | Not used | C | No | Not used | 49.707 | 3.2 | 2.5 | -0.28 | +/- 50% | Yes | 64.3773 | 4 | 18
8 | CI | <=320mm | (1900-1980] | (1900-1960] | F | Yes | 302, 323, 373, 375 | 23.969 | 2.6 | 2.5 | -0.04 | +/- 50% | Yes | 108.4736 | 4 | 13
9 | CI | <=320mm | (1900-1980] | (1950-1960] | F | Yes | 401, 421, 738, 744 | 5.2841 | 2.4 | 2.5 | 0.04 | +/- 50% | Yes | 454.1897 | 5 | 6
10 | CI | <=320mm | (1900-1980] | (1950-1960] | F | No | Not used | 38.5188 | 3 | 2.5 | -0.2 | +/- 50% | Yes | 77.884 | 4 | 16
11 | CI | <=320mm | (1900-1980] | (1960-1980] | F | Not used | Not used | 37.7794 | 1.6 | 2.5 | 0.36 | +/- 50% | Yes | 42.3512 | 3 | 28
12 | CI | <=320mm | (1900-1980] | (1920-1980] | Other | Not used | Not used | 2.5735 | 0.8 | 2.5 | 0.68 | +/- 50% | No | 310.8637 | 5 | 7 | Cohort comprises all rising mains of this material, size and function.
13 | CI | >320mm | (1900-1980] | Not used | C | Not used | Not used | 36.0847 | 2.2 | 1 | -1.2 | +/- 50% | No | 60.9677 | 3 | 21 | Cohort comprises all rising mains of this material, size and function.
14 | CI | >320mm | (1900-1980] | Not used | F | Not used | Not used | 11.5186 | 0.2 | 1 | 0.8 | +/- 50% | No | 17.3632 | 2 | 41 | Cohort comprises all rising mains of this material, size and function.
15 | CI | >320mm | (1900-1980] | Not used | S | Not used | Not used | 3.9788 | 0.2 | 1 | 0.8 | +/- 50% | No | 50.267 | 3 | 22 | Cohort comprises all rising mains of this material, size and function.
16 | DI | <=320mm | 1901 onwards | (1900-1980] | C | Not used | Not used | 15.4199 | 2.2 | 2.5 | 0.12 | +/- 50% | Yes | 142.6725 | 5 | 11
17 | DI | <=320mm | 1901 onwards | (1980-2000] | C | Not used | Not used | 21.6394 | 1.6 | 2.5 | 0.36 | +/- 50% | Yes | 73.9392 | 4 | 17
18 | DI | <=320mm | 1901 onwards | 2001 onwards | C | Not used | Not used | 29.8078 | 2.5 | 2.5 | 0 | +/- 50% | Yes | 83.8707 | 4 | 15
19 | DI | <=320mm | 1901 onwards | Not used | F | Not used | Not used | 77.8234 | 2.6 | 2.5 | -0.04 | +/- 50% | Yes | 33.409 | 3 | 32
20 | DI | <=320mm | 1901 onwards | Not used | Other | Not used | Not used | 6.1728 | 0.2 | 2.5 | 0.92 | +/- 50% | No | 32.4004 | 3 | 33 | Cohort comprises all rising mains of this material, size and function.
21 | DI | >320mm | 1901 onwards | Not used | C | Yes | Not used | 8.5253 | 1 | 1 | 0 | +/- 50% | Yes | 117.2978 | 4 | 12
22 | DI | >320mm | 1901 onwards | Not used | C | No | Not used | 81.9427 | 2.9333 | 1 | -1.9333 | +/- 50% | No | 35.7974 | 3 | 30 | Aggregating with the preceding cohort (ref 21) and ignoring Hotspot DAZ status would result in a cohort that is outside of the upper tolerance bound.
23 | DI | >320mm | 1901 onwards | Not used | F | Not used | Not used | 31.6385 | 0.7 | 1 | 0.3 | +/- 50% | Yes | 22.1249 | 2 | 39
24 | DI | >320mm | 1901 onwards | Not used | Other | Not used | Not used | 20.979 | 0.6 | 1 | 0.4 | +/- 50% | Yes | 28.6 | 2 | 36
25 | PE | <=320mm | (1900-2000] | Not used | C | Not used | Not used | 56.6576 | 2.4 | 2.5 | 0.04 | +/- 50% | Yes | 42.3597 | 3 | 27
26 | PE | <=320mm | (2000-2010] | Not used | C | Not used | Not used | 81.954 | 3.6 | 2.5 | -0.44 | +/- 50% | Yes | 43.9271 | 3 | 24
27 | PE | <=320mm | 2011 onwards | Not used | C | Yes | 251 | 0.66734 | 3.5 | 2.5 | -0.4 | +/- 50% | Yes | 5244.7086 | 5 | 2
28 | PE | <=320mm | 2011 onwards | Not used | C | Not used | 206, 273, 301, 302, 350, 373, 434, 551, 553, 701, 752 | 27.9595 | 1.2 | 2.5 | 0.52 | +/- 50% | No | 42.9192 | 3 | 26 | Aggregating with the preceding cohort (ref 27) would result in a cohort that is outside of the upper tolerance bound.
29 | PE | <=320mm | (1900-1980] | Not used | F | Not used | Not used | 77.8818 | 3.2 | 2.5 | -0.28 | +/- 50% | Yes | 41.0879 | 3 | 29
30 | PE | <=320mm | (1980-2000] | Not used | F | Not used | Not used | 51.3521 | 1.8 | 2.5 | 0.28 | +/- 50% | Yes | 35.0521 | 3 | 31
31 | PE | <=320mm | (2000-2010] | Not used | F | Not used | Not used | 105.4637 | 2.8 | 2.5 | -0.12 | +/- 50% | Yes | 26.5494 | 2 | 38
32 | PE | <=320mm | 2011 onwards | Not used | F | Not used | Not used | 50.4408 | 1.6 | 2.5 | 0.36 | +/- 50% | Yes | 31.7204 | 3 | 34
33 | PE | <=320mm | 1901 onwards | Not used | Other | Not used | Not used | 12.6612 | 2 | 2.5 | 0.2 | +/- 50% | Yes | 157.9626 | 5 | 10
34 | PL | <=320mm | 1961 onwards | Not used | C | Not used | Not used | 14.5446 | 2.4 | 2.5 | 0.04 | +/- 50% | Yes | 165.0102 | 5 | 9
35 | PL | <=320mm | (1960-2010] | Not used | F | Not used | Not used | 25.7009 | 2.4 | 2.5 | 0.04 | +/- 50% | Yes | 93.382 | 4 | 14
36 | PL | <=320mm | 2011 onwards | Not used | F | Not used | Not used | 0.1367 | 2 | 2.5 | 0.2 | +/- 50% | Yes | 14630.0831 | 5 | 1
37 | PVC | <=320mm | (1940-1980] | Not used | C | Not used | Not used | 22.1143 | 1.4 | 2.5 | 0.44 | +/- 50% | Yes | 63.3074 | 4 | 19
38 | PVC | <=320mm | 1981 onwards | Not used | C | Not used | Not used | 36.7747 | 1.6 | 2.5 | 0.36 | +/- 50% | Yes | 43.5082 | 3 | 25
39 | PVC | <=320mm | (1940-1980] | Not used | F | Not used | Not used | 53.3397 | 2.4 | 2.5 | 0.04 | +/- 50% | Yes | 44.9947 | 3 | 23
40 | PVC | <=320mm | 1981 onwards | Not used | F | Not used | Not used | 99.6795 | 3 | 2.5 | -0.2 | +/- 50% | Yes | 30.0965 | 2 | 35
41 | PVC | >320mm | (1960-2000] | Not used | C | Not used | Not used | 9.8618 | 0.2 | 1 | 0.8 | +/- 50% | No | 20.2803 | 2 | 40 | Cohort comprises all rising mains of this material, size and function.
[9 empty] | 82.4333 | 89 | 0.073783 | +/-10% | Yes

## Pareto analysis
Cohort | Rank | Total ave annual bursts | Cumulative ave annual bursts | Total sewer length (km) | Cumulative length (km)
36 | 1 | 2 | 2 | 0.1367 | 0.1367
27 | 2 | 3.5 | 5.5 | 0.66734 | 0.80404
3 | 3 | 4 | 9.5 | 1.8272 | 2.6313
6 | 4 | 2.2 | 11.7 | 3.028 | 5.6593
5 | 5 | 2 | 13.7 | 3.2953 | 8.9546
9 | 6 | 2.4 | 16.1 | 5.2841 | 14.2388
12 | 7 | 0.8 | 16.9 | 2.5735 | 16.8122
4 | 8 | 3.2 | 20.1 | 11.4639 | 28.2762
34 | 9 | 2.4 | 22.5 | 14.5446 | 42.8207
33 | 10 | 2 | 24.5 | 12.6612 | 55.482
16 | 11 | 2.2 | 26.7 | 15.4199 | 70.9019
21 | 12 | 1 | 27.7 | 8.5253 | 79.4272
8 | 13 | 2.6 | 30.3 | 23.969 | 103.3962
35 | 14 | 2.4 | 32.7 | 25.7009 | 129.097
18 | 15 | 2.5 | 35.2 | 29.8078 | 158.9048
10 | 16 | 3 | 38.2 | 38.5188 | 197.4237
17 | 17 | 1.6 | 39.8 | 21.6394 | 219.0631
7 | 18 | 3.2 | 43 | 49.707 | 268.77
37 | 19 | 1.4 | 44.4 | 22.1143 | 290.8844
1 | 20 | 1.8 | 46.2 | 28.8577 | 319.7421
13 | 21 | 2.2 | 48.4 | 36.0847 | 355.8268
15 | 22 | 0.2 | 48.6 | 3.9788 | 359.8055
39 | 23 | 2.4 | 51 | 53.3397 | 413.1452
26 | 24 | 3.6 | 54.6 | 81.954 | 495.0991
38 | 25 | 1.6 | 56.2 | 36.7747 | 531.8738
28 | 26 | 1.2 | 57.4 | 27.9595 | 559.8333
25 | 27 | 2.4 | 59.8 | 56.6576 | 616.4909
11 | 28 | 1.6 | 61.4 | 37.7794 | 654.2703
29 | 29 | 3.2 | 64.6 | 77.8818 | 732.1521
22 | 30 | 2.9333 | 67.5333 | 81.9427 | 814.0948
30 | 31 | 1.8 | 69.3333 | 51.3521 | 865.4469
19 | 32 | 2.6 | 71.9333 | 77.8234 | 943.2703
20 | 33 | 0.2 | 72.1333 | 6.1728 | 949.443
32 | 34 | 1.6 | 73.7333 | 50.4408 | 999.8838
40 | 35 | 3 | 76.7333 | 99.6795 | 1099.5633
24 | 36 | 0.6 | 77.3333 | 20.979 | 1120.5423
2 | 37 | 1.2 | 78.5333 | 44.9704 | 1165.5128
31 | 38 | 2.8 | 81.3333 | 105.4637 | 1270.9764
23 | 39 | 0.7 | 82.0333 | 31.6385 | 1302.6149
41 | 40 | 0.2 | 82.2333 | 9.8618 | 1312.4768
14 | 41 | 0.2 | 82.4333 | 11.5186 | 1323.9954

## RM threshold calcs for Ofwat
Legacy sewers | No. collapses | Ave distance between collapses | factor
CG1 | <=12 | 16 | 3.2
CG2 | <=25 | 8 | 1.6
CG3 | <=50 | 4 | 0.8
CG4 | <=100 | 2 | 0.4
CG5
Total length legacy sewer (m) | 29395368
Total no. collapses (19.16yrs) | 22573
Ave no. collapses p.a. | 1178.1315
Ave no. collapses in 5 yrs | 5890.6576
Ave distance between collapses in 5 yr period (m) | 4990.1675
RMs
Total length RMs (km) | 1323955.37
Total no. bursts (5 yrs) | 328
Ave distance between bursts in 5 yr period | 4036.4493
| Ave distance between RM bursts | No. collapses/1000km p.a/5 yr period
CG1 | 12.8 | 15.625
CG2 | 6.4 | 31.25
CG3 | 3.2 | 62.5
CG4 | 1.6 | 125
CG5
Assume 5km between collapses
Assume 4km between bursts

## lengths of zero burst RMs
AC | <=320mm |  | Other | 533.69 | 0 | 1
CI | <=320mm |  | S | 404.59 | 0 | 1
CI | >320mm |  | Other | 532.56 | 0 | 1
CO | <=320mm |  |  | 1067.89 | 0
CO | >320mm |  |  | 3468.38 | 0
DI | <=320mm |  | S | 1990.4 | 0 | 1
DI | >320mm |  | S | 1199.92 | 0 | 1
PE | >320mm |  |  | 22957.31 | 0
PE | <=320 |  | S | 9508.86 | 0 | 1
PL | >320mm |  |  | 6944.45 | 0
PL | <=320mm | 1961-2010 | Other | 731.54 | 0 | 1
PL | <=320mm |  | S | 201.98 | 0 | 1
PVC | <=320mm | 1961 onwards | S | 3608.69 | 0 | 1
PVC | <=320mm |  | Other | 3189.42 | 0 | 1
PVC | >320mm |  | F | 1290.98 | 0 | 1
PVC | >320mm |  | S | 903.8 | 0 | 1
PVC | >320mm |  | Other | 1159.09 | 0 | 1
ST | <=320mm |  |  | 6543.6 | 0
ST | >320mm |  |  | 405.36 | 0
66642.51
<=320mm | 7611.49
>320mm | 33775.5